### Part I – General

- Product Specification

The Ducted Heat Recovery Ventilator shall be as manufactured by "Systemair" or approved equal provided all specifications are met. Systemair ERV commercial series shall be used as the basis of design.

- Requirements

  - Unit shall be listed to safety standard UL 1812, Ducted Heat Recovery Ventilators.

  - Performance shall be as scheduled on plans.

  - Exhaust discharge hood shall have integrated backdraft damper.

  - The unit shall be capable of operating in winter and summer conditions without any loss of ventilation capacity.

  - The Energy recovery wheel shall be of aluminum counter flow construction type coated with a thin non-migrating adsorbent layer.

  - The fans shall be external-rotor motorized impellors powered by electronically-commutated (EC) motors, controlled by a provided potentiometer or by a 0-10 VDC or 4-20 mA signal provided by others.

### Part II – Product

### Cabinet

- Cabinet shall be constructed of G90 galvanized, 22-gauge steel sheet. All seams shall be sealed, requiring no caulking at job site.

- Unit casing shall be double wall with 25mm (1 inch) fiberglass insulated. The flame spread index of the insulation material shall not be over 25 and its smoke developed index shall not be over 50 when tested in accordance with the Standard for Tests for Surface Burning Characteristics of Building Material, UL723.

### Weather hoods

- Weather hoods shall be constructed of G90 galvanized, 20-gauge steel sheet.

- The fresh air weather hood shall be protected by MERV1 washable filter.

- Weather hoods shall be designed to prevent wet snow and large water droplets from entering the unit.

- The fresh air weather hood shall maintain a face velocity less than 1.6 m/s (340 ft/min).

### Energy Recovery Wheel

### The rotor matrix shall be made of a corrosion resistant aluminum alloy that is composed of alternating corrugated and flat, continuously wound layers of uniform widths; that guarantees laminar air flow, and low static pressure loss. The rotor wheel shall be reinforced with spokes, welded at the hub and perimeter to prevent any uneven run out during normal operations. All corrugated surface shall be coated with a thin non-migrating adsorbent layer. The wheels effectiveness shall be clearly documented in accordance with ASHRAE 84 and AHRI 1060 standards. The flame spread index of the energy recovery wheel shall not be over 25 and its smoke development index shall not be over 50 when tested in accordance with the Standard for Tests for Surface Burning Characteristics of Building Material, UL723

### Electrical

      - Electrical box shall be isolated from the airflows and all integral wires and connections protected.

      - All internal electrical components shall be factory wired for single point power connection. When equipped with Electric pre-heater option, a second point connection will be required

      - All electrical components shall be UL Listed or Recognized.

### Fan Sections & Motors

- Fans shall be backward inclined motorized impellers.

- Motors shall be electronic-commutate (EC), controlled by a provided potentiometer or by a 0-10 VDC or 4-20 mA signal provided by others.

- Fan motor shall have maintenance-free permanently lubricated sealed ball bearings.

- Fan motor shall be (TOP) thermal overload protected.

- Fan motor shall be UL listed to UL1004 and/or UL2111, CSA C22.2 No. 77 and No.100.

- Fan motor shall have IP protection class 44 or 54 according to DIN 40 050.

- Separate fans for exhaust and supply blowers shall be provided.

### Filters

              - The outdoor air shall be protected by MERV13 50mm (2 inches) or 95mm (3.75 inches) pleated filters constructed to meet UL 900.

              - The return air shall be protected by MERV8 50mm (2 inches) or 44mm (1.75 inches) pleated filters constructed to meet UL 900.

### PART – III Execution

### Serviceability

  - Unit shall have hinged and/or screwed access panels on front.

  - Energy recovery wheel, filters and motors shall be serviceable from the front of the unit.

  - Fan assemblies shall be mounted on a removable sliding base. Energy recovery wheel and filters shall be mounted in slide-out rails for ease of inspection, removal, and cleaning.

- Installation

- Unit shall be seated on a roof curb or on a platform.

- Openings shall be provided for suitable ductwork connection.

### Warranty

The ducted heat recovery ventilator shall be warranted to be free from defects in material, workmanship and on all parts for a period of 3 year from the purchase date. The energy recovery wheel shall be warranted to be free from defects in material and workmanship for a 3 years period under circumstances of normal use.

TBD.Sept 2009